## vicki-mapping
##general
version | max_downlink_commands
1.0 | 5
##models
name | selectors
all | { mId: vicki }
others
##objects
id | name | value | type | access_mode | value_type | precision | units | cov_increment | min_value | max_value | models | description
reason | Reason of uplink | 0 | number | R | UINT8 |  |  | 1 |  |  | all | Reason
targetTemperature | Target temperature in Celsius | 0 | number | R | FLOAT | 2 | Cel | 0.1 |  |  | all | Target temperature in °C
sensorTemperature | Sensor temperature in Celsius | 0 | number | R | FLOAT | 2 | Cel | 0.1 |  |  | all | Temperature in °C
relativeHumidity | Relative humidity in percentage | 0 | number | R | FLOAT | 2 | %RH | 0.1 |  |  | all | Relative humidity in RH
motorPosition | Motor position in steps | 0 | number | R | FLOAT | 2 |  | 0.1 | 0 | 15 | all | Motor position in steps
motorRange | Motor range in steps | 0 | number | R | FLOAT | 2 |  | 0.1 | 0 | 15 | all | Motor range in steps
batteryVoltage | Battery voltage | 0 | number | R | FLOAT | 2 | V | 0.1 |  |  | all | Battery voltage in volts
openWindow | Open window is detected | 0 | boolean | R | BOOL | [5 empty] | all | Open window is detected
childLock | Child lock | false | boolean | R | BOOL | [5 empty] | all | Child lock option is enabled
highMotorConsumption | High motor consumption flag | false | boolean | R | BOOL | [5 empty] | all | High motor consumption is detected
lowMotorConsumption | Low motor consumption flag | false | boolean | R | BOOL | [5 empty] | all | Low motor consumption is detected
brokenSensor | Broken sensor flag | false | boolean | R | BOOL | [5 empty] | all | Broken sensor is detected
openWindow:enabled | Open window detection enabled | false | boolean | R | BOOL | [5 empty] | all | Open window detection is activated
openWindow:duration | Open window detection duration | 0 | number | R | UINT16 |  | minutes | 1 |  |  | all | Open window duration in minutes
openWindow:motorPosition | Open window detection motor position | 0 | number | R | UINT16 |  |  | 1 |  |  | all | Open window motor position
openWindow:delta | Open window detection delta | 0 | number | R | UINT8 |  |  | 0.1 | 0 | 255 | all | Open window delta
temperatureRangeSettings:min | Min temperature | 0 | number | R | UINT8 |  | Cel |  | 0 | 255 | all
temperatureRangeSettings:max | Max temperature | 0 | number | R | UINT8 |  | Cel |  | 0 | 255 | all
internalAlgoParams:period | Internal algo params period | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
internalAlgoParams:pFirstLast | Internal algo params pFirstLast | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
internalAlgoParams:pNext | Internal algo params pNext | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
internalAlgoTdiffParams:warm | Internal algo tdiff params warm | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
internalAlgoTdiffParams:cold | Internal algo tdiff params cold | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
operationalMode | Operational mode | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
joinRetryPeriod | Join retry period | 0 | number | R | FLOAT | 2 |  | 0.1 |  |  | all
uplinkType | Uplink type | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
watchDogParams:wdpC | Watchdog params wdpC | 0 | number | R | UINT16 |  |  | 1 |  |  | all
watchDogParams:wdpUc | Watchdog params wdpUc | 0 | number | R | UINT16 |  |  | 1 |  |  | all
primaryOperationalMode | Primary operationnal mode | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
batteryRangesBoundaries:Boundary1 | Battery ranges boundary 1 | 0 | number | R | UINT16 |  |  | 1 |  |  | all
batteryRangesBoundaries:Boundary2 | Battery ranges boundary 2 | 0 | number | R | UINT16 |  |  | 1 |  |  | all
batteryRangesBoundaries:Boundary3 | Battery ranges boundary 3 | 0 | number | R | UINT16 |  |  | 1 |  |  | all
batteryRangesOverVoltage:Range1 | Battery ranges over voltage range 1 | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
batteryRangesOverVoltage:Range2 | Battery ranges over voltage range 2 | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
batteryRangesOverVoltage:Range3 | Battery ranges over voltage range 3 | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
OVAC | OVAC | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all
manualTargetTemperatureUpdate | Manual target temperature update | 0 | number | R | UINT8 |  | Cel |  | 0 | 255 | all
keepAliveTime | Keep alive time | 0 | number | R | UINT8 |  |  | 1 | 0 | 255 | all | PI run period
deviceVersions:hardware | Hardware version | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all | Hardware version
deviceVersions:software | Software version | 0 | number | R | UINT8 |  |  |  | 0 | 255 | all | Software version
setKeepAlive | Set keep alive time command | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all
getKeepAliveTime | Get keep alive time command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
recalibrateMotor | Recalibrate moto command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
getDeviceVersions | Get device versions command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setOpenWindow:enabled | Set open window enabled | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all | 1 if we want to enable it or 0 if we want to disable it
setOpenWindow:closeTime | Set open window close time | 0 | number | RW | FLOAT | 1 | minutes | 0.1 |  |  | all | for how long should the device keep the set motor position after it detected an open window event (example value: 20 (if we want to have the Vicki at the defined position for 20 minutes))
setOpenWindow:delta | Set open window delta time | 0 | number | RW | UINT16 |  | Cel | 1 | 0 | 65535 | all | the value of the desired difference in the measured temperature (degrees in Celsius)
setOpenWindow:motorPosition | Set open window motor position | 0 | number | RW | UINT16 |  |  | 1 | 0 | 65535 | all | the motor position of the device for the specified time after an open window event was detected
getOpenWindowParams | Get open window params command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setChildLock | Set child lock command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all | 1 if we want to enable it or 0 if we want to disable it
getChildLock | Get child lock command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setTemperatureRange:min | Set temperature range min | 0 | number | RW | UINT8 |  | Cel | 1 | 5 | 30 | all | the minimum value for the device range (between 5 and 30)
setTemperatureRange:max | Set temperature range max | 0 | number | RW | UINT8 |  | Cel | 1 | 5 | 30 | all | the maximum value for the device range (between 5 and 30)
getTemperatureRange | Get temperature range command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
forceClose | Force close command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setInternalAlgoParams:pFirstLast | Set internal algo params pFirstLast | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all | steps
setInternalAlgoParams:pNext | Set internal algo params pNext | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all | steps
getInternalAlgoParams | Get intenal algo params command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setInternalAlgoTdiffParams:cold | Set internal algo tdiff cold | 0 | number | RW | UINT8 |  | Cel | 1 | 0 | 255 | all | in °C
setInternalAlgoTdiffParams:warm | Set internal algo tdiff warm | 0 | number | RW | UINT8 |  | Cel | 1 | 0 | 255 | all | in °C
getInternalAlgoTdiffParams | Get internal algo tdiff params command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setOperationalMode | Set operational mode command | 0 | number | RW | UINT8 |  |  | 1 | 0 | 2 | all | 0 - Online manual control mode. Default for the device, 1 - Online automatic control mode, 2 - Online automatic control mode with external temperature reading.
getOperationalMode | Get operational mode command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setTargetTemperature | Set target temperature command | 0 | number | RW | UINT8 |  | Cel | 1 | 5 | 30 | all | digits in range 5-30
setExternalTemperature | Set external temperature command | 0 | number | RW | UINT8 |  | Cel | 1 | 5 | 30 | all | digits in range 5-30
setJoinRetryPeriod | Set join retry period command | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all | minutes, cannot be 0
getJoinRetryPeriod | Get join retry period command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setUplinkType | Set uplink type command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all | 0 - unconfirmed, 1 - confirmed
getUplinkType | Get uplink type command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setTargetTemperatureAndMotorPosition:motorPosition | Set target temperature and motorPosition | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all | range 0 to motorRange
setTargetTemperatureAndMotorPosition:targetTemperature | Set target temperature and targetTemperature | 0 | number | RW | UINT8 |  | Cel | 1 | 5 | 30 | all | digits in range 5-30
setWatchDogParams:confirmedUplinks | Set watchdog params confirmedUplinks | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all
setWatchDogParams:unconfirmedUplinks | Set watchdog params unconfirmedUplinks | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all
getWatchDogParams | Get watchdog params command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setPrimaryOperationalMode | Set primary operational mode command | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all | 0 - Online manual control mode. Default for the device, 1 - Online automatic control mode, 2 - Online automatic control mode with external temperature reading.
getPrimaryOperationalMode | Get primary operational mode command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setProportionalAlgorithmParameters:coefficient | Set proportional algorithm parameters coefficent | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all
setProportionalAlgorithmParameters:period | Set proportional algorithm parameters period | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all
getProportionalAlgorithmParameters | Get proportional algorithm parameters command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setTemperatureControlAlgorithm | Set temperature control algorithm command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all | 0 - Proportional, 1 - Equal
getTemperatureControlAlgorithm | Get temperature control algorithm command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setMotorPositionOnly | Set motor position only command | 0 | number | RW | UINT16 |  |  | 1 | 0 | 65535 | all | range 0 to motorRange
deviceReset | Device reset command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setChildLockBehavior | Set child lock behavior command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all | 0 - Child lock is automatically disabled when the device goes offline, 1 - Child lock remains unchanged when the device goes offline
getChildLockBehavior | Get child lock behavior command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setProportionalGain | Set proportional gain command | 0 | number | RW | FLOAT | 2 |  | 0.1 |  |  | all
getProportionalGain | Get proportional gain command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setExternalTemperatureFloat | Set external temperature float command | 0 | number | RW | FLOAT | 2 | Cel | 0.1 |  |  | all
setIntegralGain | Set integral gain command | 0 | number | RW | FLOAT | 2 |  | 0.1 |  |  | all
getIntegralGain | Get integral gain command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setPiRunPeriod | Set PI run period command | 0 | number | RW | UINT8 |  | minutes | 1 | 0 | 255 | all | in minutes
getPiRunPeriod | Get PI run period command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setTempHysteresis | Set temp hysteresis command | 0 | number | RW | UINT8 |  |  | 1 | 0 | 255 | all
getTempHysteresis | Get temp hysteresis command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setOpenWindowPrecisely:enable | Set open window precisely enable | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 255 | all
setOpenWindowPrecisely:duration | Set open window precisely duration | 0 | number | RW | UINT16 |  | minutes | 1 | 0 | 65535 | all | in minutes
setOpenWindowPrecisely:delta | Set open window precisely delta | 0 | number | RW | UINT16 |  |  | 1 | 0 | 65535 | all
getOpenWindowPrecisely | Get open window precisely command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
setForceAttach | Set force attach command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all | 0: disabled, 1: enabled
getForceAttach | Get force attach command | 0 | binary | RW | UINT8 |  |  | 1 | 0 | 1 | all
sendCustomHexCommand | Send custom hex command command | "" | string | RW | STRING | [5 empty] | all | Hexa payload as string like '014F32'