## Feuil1
##general
version | max_downlink_commands
1.0 | 5
##models
name | selectors
all | { mId: sab07 }
others
##objects
id | name | value | type | access_mode | value_type | precision | units | cov_increment | min_value | max_value | models | description
targetTemperature | Target temperature | 0 | number | R | FLOAT | 2 | Cel | 0.1 |  |  | all | Target temperature in °C
sensorTemperature | Temperature | 0 | number | R | FLOAT | 2 | Cel | 0.1 |  |  | all | Temperature in °C
relativeHumidity | Relative humidity | 0 | number | R | FLOAT | 2 | %RH | 0.1 |  |  | all | Relative humidity in RH
motorPosition | Motor position | 0 | number | R | FLOAT | 2 | deg | 0.1 | 0 | 15 | all | Motor position in °
motorRange | Motor range | 0 | number | R | FLOAT | 2 | deg | 0.1 | 0 | 15 | all | Motor range in °
batteryVoltage | Battery voltage | 0 | number | R | FLOAT | 2 | V | 0.1 |  |  | all | Battery voltage in volts
statusFlags:openWindow | Open window flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Open window flag (0: closed 1: open)
statusFlags:highMotorConsumption | High motor consumption flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | High motor consumption flag (0: no alarm, 1: alarm)
statusFlags:lowMotorConsumption | Low motor consumption flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Low motor consumption flag
statusFlags:brokenSensor | Broken sensor flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Broken sensor flag (0: no alarm, 1: alarm)
extraFlags:manualTempDisabled | Manual temperature disabled flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Manual temperature disabled flag
extraFlags:motorCalibrationFailed | Motor calibration failed flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Motor calibration failed flag (0: no alarm, 1: alarm)
extraFlags:deviceAttachedToBackplate | Device attached to backplate flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Device attached to backplate flag
extraFlags:deviceOnline | Device online flag | 0 | binary | R | UINT8 |  | state |  |  |  | all | Device online flag (0: no alarm, 1: alarm)
proportionalAlgorithmParameters | Proportional algorithm parameters | 0 | number | R | FLOAT | 2 |  | 0.1 | 0 | 255 | all | Proportional algorithm parameters
integralGain | Integral gain | 0 | number | R | FLOAT | 2 |  | 0.1 |  |  | all | Integral gain
integralValue | Integral value | 0 | number | R | FLOAT | 2 |  | 0.1 |  |  | all | Integral value
piRunPeriod | PI run period | 0 | number | R | FLOAT | 2 |  | 0.1 | 0 | 255 | all | Keep alive period in minutes
keepAlivePeriod | Keep alive period | 0 | number | R | FLOAT | 2 |  | 0.1 | 0 | 255 | all | PI run period
temperatureHysteresis | Hysteresis temperature | 0 | number | R | FLOAT | 2 |  | 0.1 |  |  | all | Hysteresis temperature
hardwareVersion | Hardware version | "" | string | R | STRING | [5 empty] | all | Hardware version
softwareVersion | Software version | "" | string | R | STRING | [5 empty] | all | Software version
watchdogParameters:confirmedValue | Watchdog confirmed value | 0 | number | R | UINT8 |  |  | 1 | 0 | 255 | all | Watchdog confirmed value
watchdogParameters:unconfirmedValue | Watchdog unconfirmed value | 0 | number | R | UINT8 |  |  | 1 | 0 | 255 | all | Watchdog unconfirmed value
targetWithRange | Target temperature with range | 0 | number | RW | FLOAT | 1 | Cel | 0.1 |  |  | all
externalTemperature | External temperature | 0 | number | RW | FLOAT | 1 |  | 0.1 |  |  | all
operationalMode | Operational mode | 0 | number | RW | UINT8 |  |  | 1 | 0 | 2 | all | Operational mode (0: manual, 1: auto, 2: forced)
recalibrateMotor | Motor recalibration | false | boolean | RW | BOOL |  |  | 1 |  |  | all | Motor recalibration
motorPosition | Motor position | 0 | number | RW | FLOAT | 1 |  | 1 | 0 | 65535 | all | Motor position, take care to also update targetTemperature, they must be part of the same downlink
targetTemperature | Target temperature | 0 | number | RW | FLOAT | 1 | Cel | 0.1 |  |  | all | Target temperature, take care to also update motorPosition, they must be part of the same downlink
openWindowDetection:enable | Open window detection enable | 0 | binary | RW | UINT8 | [5 empty] | all
openWindowDetection:duration | Open window detection duration | 0 | number | RW | FLOAT | 1 | minute | 0.1 | 0 | 255 | all | Open window detection in minutes
openWindowDetection:tempDelta | Open window detection delta temperature | 0 | number | RW | FLOAT | 1 |  | 0.1 | 0 | 255 | all | Open window detection delta temperature in tenths of degrees Celsius
keepAlivePeriod | Keep alive period | 0 | number | RW | FLOAT | 1 | minute | 0.1 | 0 | 255 | all | Keep alive period in minutes
childLock | Child lock | 0 | binary | RW | UINT8 | [5 empty] | all | Child lock activation
resetDevice | Device reset | false | boolean | RW | BOOL | [5 empty] | all | Reset the device
piAlgorithm:proportionalGain | PI algorithm proportional gain | 0 | number | RW | FLOAT | 1 |  | 0.1 |  |  | all | PI algorithm proportional gain
piAlgorithm:integralGain | PI algorithm integral gain | 0 | number | RW | FLOAT | 1 |  | 0.1 |  |  | all | PI algorithm integral gain